## Sheet1
MMR Generation
Power Plant | Units | Reason
PP9-E & Ext2 | 4-8 units | AGC
Layla | 0-4 units | To Control Line Flow (based on previous day Pattern), after commissioning of statcom , Layla MMR (N - 1) = Load of Layla Town - 80
Qassim | 2 units | Minimum requirement on 132 KV Network
Hail2 | 1 Min unit
Jouf | 1 Min unit | Based on Equation 0.35*Load (Jouf+Arar+Tabarjal+Qurayat+Wdshamal+Tabuk+Duba+Madain) Max 650MW
Arar | 1 Min unit | Based on 132 KV Line limit 40MW and 0.35*Load (Jouf+Arar+Tabarjal+Qurayat+Wdshamal+Tabuk+Duba+Madain) Max 650MW (N-2)
Qurrayat | 3 Min units | Based on Import from Jouf Equation 0.35* Load (Tabarjal+Qurayat+Wdshamal+Tabuk+Duba+Madain) Max 500 MW (N-2)
Tabuk |  | Based on Import from Tabarjal 0.35*Load(Tabuk+Duba+Madain) Max 250 MW (N-2)
Duba |  | Based on Import from Tabuk 0.30* Load(Duba + Madain ) Max 120 MW
Alwajh | 2 units | Based on Import from Duba 0.20* Load of ( Madain+Wajh+AlUla ) but shall not exceed 110 MW
Juba |  | Juba Load Demand - 150
Jazan | 3 Min units | Based on Equation 0.5374*Load (Jazan+Najran) - 541 - Najran GEN
Najran | 3-4 units | Depending on Fuel availability
Tihama |  | Based on Equation 0.3215*Load Tihama -55
Asir |  | Based on Equation 0.4263 x Asir load (MW) -214.2
Transfer Between Areas And SubAreas
Line |  | Limit
EOA TO COA |  | 8400MW + [0.2897xPP10] + [0.4233xFaras] - [0.1635xCOA Demand].but shall not exceed 6000MW. UPDATED FOR SUMMER SESSON with 5% margin
COA TO WOA |  | 0
WOA TO COA |  | 0
WOA TO SOA |  | (N-2) (0.0787 * SOA load +1243).
Bisha TO Juba |  | MAX = 150 MW (if 2 circuits in service)
Juba TO Bisha |  | MAX = 50 MW
Riyadh TO Qassim |  | (4917-0.2887* Qassim load) , MAX = 4500 MW [N-2].
Qassim TO Hail |  | MAX = 1300 MW
Hail TO jouf |  | 0.35*Load (Jouf+Arar+Tabarjal+Qurayat+Wdshamal+Tabuk+Duba+Madain+Wajh+AlUla) but shall not exceed 650MW (N-2)
Jouf TO Arar |  | No limit
Arar TO Jouf |  | No limit
Jouf TO Tabarjal |  | 0.35* Load of (Tabarjal+Qurayat+Wdshamal+Turaif+Tabuk+Duba+Madain+Wajh+AlUla) but shall not exceed 500 MW (N-2)
Tabarjal TO Tabuk |  | 0.35* Load of (Tabuk+Duba+Madain+Wajh+AlUla) but shall not exceed 250 MW
Tabuk TO Duba |  | 0.30* Load of (Duba + Madain+Wajh+AlUla) but shall not exceed 120 MW
Duba TO Wajh |  | 0.20* Load of ( Madain+Wajh+AlUla ) but shall not exceed 110 MW
Reserve Requirement for Areas and SubAreas
Area |  | Minimum spinning reserve requirement
EOA |  | 190 MW [ Primary =90 MW , Secondary =100 MW ]
COA |  | 170 MW [ Primary =70 MW , Secondary =100 MW ]
WOA |  | 245 MW [ Primary =170 MW , Secondary =75 MW ]
SOA |  | 110 MW [ Primary =60 MW , Secondary =50 MW ]
NEOA |  | 0 MW [ Primary =0 MW , Secondary =0 MW ]
NWOA |  | 0 MW [ Primary =0 MW , Secondary =0 MW ]